| Title | Temperature Control 2-PID Function Block for CP1W-TS Expansion Units |
| --- | --- |

| Basic Function | The Temperature Control 2-PID Function Block for the CP1W-TS expansion units realizes 2-PID control for the Compact CP1 Programmable Logic Controllers. The 2-PID simultaneously achieves two characteristics, set point tracking and disturbance suppression. |
| --- | --- |
| Symbol |  |
| File Name | TC_2PID_function_block.cxf |
| Developed by | Omron Europe |
| Release Date | 28 July 2026 |
| Supported Models | Model Input Description - CP1W-TS001 2 Thermocouple Type K or J Inputs - CP1W-TS002 4 Thermocouple Type K or J Inputs - CP1W-TS003 4 Thermocouple Type K or J Inputs (Input 3 and 4 can also operate as Analog Input; 0 to 10V, 1 to 5V or 4 to 20 mA) - CP1W-TS004 12 Thermocouple Type K or J Inputs - CP1W-TS101 2 Platinum Resistance Thermometer Type Pt100 or JPt100 Inputs - CP1W-TS102 4 Platinum Resistance Thermometer Type Pt100 or JPt100 Inputs |
| Conditions for Usage | - P_On (Always On Bit) should be connected to the EN input. - The Enable input operates the PID Control. - All input parameters should confirm the specification range. |
| Function Description | The TC_2PID_function_block adds PID Control with Auto-Tuning feature for the CP1W-TS expansion units. Prerequisite for the Function Block to operate correctly, P_On (Always On Bit) should be connected to the EN Input. The PLC evaluates the function block status every PLC cycle. Simultaneously the Control Output is not operating unless the Enable input is on, thus preventing uncontrolled execution of any equipment controlled by the PID Control. The Process Value input is of sensor input type Thermocouple, Platinum Resistance Thermometer or Analog. The Set Point is user defined and related based on the type of sensor input plus the operating range of the sensor input. The operating range may differ per sensor type. The maximum and minimum parameters contain the operating range of the sensor input. Please consult the specific sensor datasheet for the accurate operating range. The P, I, D and Control Period parameters determine the responsiveness of the PID Control function. The P, I and D parameters can be configured using two different methods. The first method is configuring the parameters manually. The second method automatically detects the ideal parameters using the built-in Auto-Tuning feature. While the Auto-Tuning process is in progress, the Auto-Tuning Status Bit is on. Once the Auto-Tuning is completed, the Auto-Tuning Status Bit is off and P, I and D Output parameters show the result of the Auto-Tuning process. Starting and stopping of the Auto-Tuning process is executed manually. The Control Period parameter defines the responsiveness of the Control Output. It evaluates at specified time interval the output status of the 2PID function. Errors generated by the TC_2PID_function_block cause the Control Output to stop operating. In the event of an error, the Error Bit is on and the status code shall adjust accordingly. In order to continue the 2PID Control Function, the error has to be reset manually. |
| FB precautions | - Switching off the Enable input causes the Control Output to turn off. - Invalid input values prohibit the Control_Output from operating. It remains off until the input parameters are within the correct range and resetting the error. - Invalid P, I and D parameters shall execute an Auto-Tuning process when attempting to enable the Function Block. - It is required to acknowledge an error using the Reset_Error input before the Function Block can operate. |
| EN Input Condition | Connect P_On (Always On Bit) to EN Input in order to operate the Function Block. |
| Restrictions Input Variables Output Variables | - Control_Period has an operating range from 1.00 to 99.99 seconds. - Filter_Coefficient has input range from α = 0.00 to 0.99 (#0100 to #0163). - Maximum and Minimum Set Point Values should be consistent with the connected Temperature Sensor. - The differential up of Start_AT and Stop_AT start or stop the Auto-Tuning process. - AT_Status turns automatically off once the Auto-Tuning process is completed. - The OUT_P, OUT_I and OUT_D variables display the used PID parameters. |
| Status Codes | Status Code Description - #0000 No Error or Normal Operation - #0001 Manually Aborted Auto-Tuning - #0002 Manually Started Auto-Tuning - #0600 Invalid Input Entry at Control Period Input - #0601 Invalid PID parameter Settings detected - #0602 Invalid Input Entry at Minimum and/or Maximum Parameter Inputs - #0603 Invalid Input Entry at Filter Coefficient (2-PID parameter) Input |
| Application Example 1 : Applying Thermocouple Input as Process Value | - Please confirm that all parameters are set and are within the range specification. Otherwise, an error occurs depending on what input parameter is invalid. - The data range at the Process Value that include one digit after the decimal point are stored without the decimal point, i.e., 10 times the actual value is stored, e.g. Unit: 0.1C° -> 500.0 C° = &5000 = #1388. - The Set Point parameter is the target value were the PID control focuses. Additional parameters related to Set Point are Maximum and Minimum parameters. They define the maximum and minimum range for the Set Point parameter. - The PID parameters can be configured manually using P_Input, I_Input and D_Input. The Write_PID_Inputs input is required to write the PID input parameters. - If no PID parameters are stored, the function block shall generate a #0601 error when attempting to enable the 2-PID function. The user can manually start the Auto-Tuning Process causing the status code #0002 to occur. While the Auto-Tuning process in ongoing, the AT_Status bit is turned on and will turn off when the Auto-Tuning process has been completed. - OUT_P, OUT_I and OUT_D parameters are used as User Data Information outputs to inform the user what PID parameters are applicable for the PID function. - The Control Period parameter defines the responsiveness of the Control Output. The operating range is 1.00 to 99.99 seconds. For example, when the Control Period is set to #0064 = &100 (1 second), the PID function evaluates every 1 second whether to switch on or off the Control_Output. - The Error Bit turns on when an error has occurred. Please refer to Status Codes for detailed information regarding what type of error has occurred. |
| Application Example 2 : Applying Analog Input as Process Value - CP1W-TS003 only | - Please confirm that all parameters are set and are within the range specification. Otherwise, an error occurs depending on what input parameter is invalid. - The data range at the Process Value is based on the Analog Input. For example, 4 to 20 mA is converted into #0000 to #2EE0. - The Set Point parameter is the target value were the PID control is focused. Additional parameters related to Set Point are Maximum and Minimum parameters. They define the maximum and minimum range for the Set Point parameter. - The PID parameters can be configured manually using P_Input, I_Input and D_Input. The Write_PID_Inputs input is required to write the PID input parameters. - If no PID parameters are stored, the function block shall generate a #0601 error when attempting to enable the 2-PID function. The user can manually start the Auto-Tuning Process and a status code of #0002 shall occur. While the Auto-Tuning process in ongoing, the AT_Status bit is turned on and will turn off when the Auto-Tuning process has been completed. - OUT_P, OUT_I and OUT_D parameters are used as User Data Information outputs to inform the user what PID parameters are applicable for the PID function. - The Control Period parameter defines the responsiveness of the Control Output. The operating range is 1.00 to 99.99 seconds. For example, when the Control Period is set to #0064 = &100 (1 second), the PID function evaluates every 1 second whether to switch on or off the Control_Output. - The Error Bit turns on when an error has occurred. Please refer to Status Codes for detailed information regarding what type of error has occurred. |

 Variable Tables

## Input Variables

| Name | Variable name | Data type | Default | Setting Range | Description |
| --- | --- | --- | --- | --- | --- |
| EN | EN | BOOL |  |  | To control execution of the Function Block |
| Activate PID Function | Enable | BOOL |  | 0, 1 | Enable the PID function |
| Process Variable | Process_Value | INT |  | -32768 to 32767 | Sensor Input Signal |
| Set Variable | Set_Point | INT | 0 | -32768 to 32767 | Define Set Point value |
| Maximum Set Variable | Maximum | INT | 32767 | Min to 32767 | Define maximum Set Point value |
| Minimum Set Variable | Minimum | INT | -32768 | -32768 to Max | Define minimum Set Point value |
| Execute Auto-Tuning | Start_AT | BOOL | 0 | 0, 1 | Execute the Auto-Tuning process. |
| Stop Auto-Tuning | Stop_AT | BOOL | 0 | 0, 1 | Manual Stop the Auto-Tuning process. |
| Control Period for Output: Control_Output | Control_Period | WORD | #0064 | #0064 to #270F (1.00 to 99.99 sec.) | Define the control period for Control_Output. For example, #0064 is 1 second. The state of Control_Output is evaluated every 1 second. |
| Proportional Band Input | P_Input | INT |  | #0001 to #270F | Manually configure the “P” parameter for the PID function. |
| Integral Input | I_Input | INT |  | #0001 to #1FFF | Manually configure the “I” parameter for the PID function. |
| Derivative Input | D_Input | INT |  | #0001 to #1FFF | Manually configure the “D” parameter for the PID function. |
| Apply PID Input Values | Write_PID_Inputs | BOOL | 0 | 0, 1 | Write the manually configured PID parameters to the PID Control Function. |
| 2PID Parameter | Filter_Coefficient | WORD | 0 | #0000, #0100 to #0163 | #0000 : α = 0,65 (default) Setting from #0100 to #0163 : α = 0,00 to α = 0,99 |
| Reset Error | Reset_Error | BOOL | 0 | 0, 1 | Reset active error. |

## Output Variables

| Name | Variable name | Data type | Description |
| --- | --- | --- | --- |
| ENO (May be omitted.) | ENO | BOOL | 1 (ON) : Function Block processed normally. 0 (OFF) : Function Block not processed or ended in an error. |
| Auto-Tuning Status Bit | AT_Status | BOOL | 1 (ON) : Auto-Tuning process operational 0 (OFF) : Auto-Tuning process NOT operational |
| Control Output | Control_Output | BOOL | PID Control Output |
| Error Status Bit | Error | BOOL | 1 (ON) : Error Exist 0 (OFF) : Normal Operation |
| Error Code Information | Status_Code | INT | #0000 : No Error or Normal Operation #0001 : Manually Aborted Auto-Tuning #0002 : Manually Started Auto-Tuning #0600 : Invalid Input Entry at Control Period Input #0601 : Invalid PID parameter Settings detected #0602 : Invalid Input Entry at Minimum and/or Maximum Parameter Inputs #0603 : Invalid Input Entry at Filter Coefficient (2PID parameter) Input |
| Auto-Tuning Proportional Band Output | OUT_P | WORD | “P” parameter used by the PID Control Function. The parameter is written manually or by the Auto-Tuning process. |
| Auto-Tuning Integral Output | OUT_I | WORD | “I” parameter used by the PID Control Function. The parameter is written manually or by the Auto-Tuning process. |
| Auto-Tuning Derivative Output | OUT_D | WORD | “D” parameter used by the PID Control Function. The parameter is written manually or by the Auto-Tuning process. |

 Version History

| Version | Date | Contents |
| --- | --- | --- |
| 1.00 | 3-September-2015 | Original production |